Antigneous Instruction Manual
Written by Lexzach
What is this?
Antigneous is an affordable, open-source fire alarm control panel (FACP). This is targeted towards hobbyists or areas that do not have the privilege of having an fire alarm system from a name-brand company.
Disclaimer!
Antigneous is not officially approved for use as a fire alarm system. Although the creator has done everything they can to make sure the panel will work with zero issues, this cannot be guaranteed without extensive testing by official parties. If you do not accept the inherent risk of using a non-approved fire alarm system. DO NOT USE THIS.

# Getting Started
# Fail-safe Mode
Fail-safe mode is a specific mode included with the Antigneous panel. If your panel fails to boot, either from an error loading settings or something else. Fail-safe mode is intended to be a completely separate environment that is designed to boot up without fail. It does not require any interaction with the saved settings, and skips almost all of the boot-up code.
When the panel is in fail-safe mode, features are extremely limited. The only thing that works is the horn relay, strobe relay, smoke detector relay, silence button, and reset button. The reset button is the only thing that the user can interact with when the alarms are off, the reset button will restart the panel. When the alarms are on, the silence button can also be used to perform an audible silence. The coding on the alarms in fail-safe mode is continuous, and there is no verification or end-of-line resistor checks.
Fail-safe mode is not ideal to be in, and as the name suggests, is simply a mode that the panel can be in that ensures there is always fire detection, even if the panel is entirely unable to boot normally. Fail-safe mode should absolutely not be considered normal operation, and the reason for the panel not booting normally should be found and fixed immediately.
# Error Codes
Antigneous Error Codes
Error Code	Meaning	Solutions
1	The panel’s settings have failed a validity check and must be reset to factory settings.	Press the reset button to boot into the fail-safe mode. / Press the drill button to reset the panel to factory settings.
2	The panel’s firmware has been updated to a new version, and must be reset to factory settings in order to add new settings into the panel EEPROM.	Press the reset button to boot into the fail-safe mode. / Press the drill button to reset the panel to factory settings.