Antigneous TECHNICAL Instruction Manual
IMPORTANT:
Make sure you are up to date.
Check this on line 6 of main.cpp
EEPROM Version: 1.1
Should I be reading this?
This is the technical instruction manual for the operation of the Antigneous fire alarm control panel (FACP). This manual will go very in-depth. If you just want the regular instructions, please read the non-technical instruction manual.
Disclaimer!
Antigneous is not officially approved for use as a fire alarm system. Although the creator has done everything they can to make sure the panel will work with zero issues, this cannot be guaranteed without extensive testing by official parties. If you do not accept the inherent risk of using a non-approved fire alarm system. DO NOT USE THIS.

END OF PAGE

The brains of Antigneous
Antigneous runs off of an ESP-32 Dev Kit V1. This board offers many features that are not present on other boards. This board even includes built in WiFi, which may be used in the future.
Antigneous Pinout
Zone 1	15
Zone 2	39
Horn Relay	13
Strobe Relay	18
Smoke Relay	14
Panel Buzzer	4
Ready LED	27
Silence LED	26
Alarm LED	25
Key Switch	33
Reset Button	32
Silence Button	35
Drill Button	34
SCL (LCD)	22
SDA (LCD)	21

EOL Resistors and Ground Faults
Antigneous is able to detect ground faults through the use of end-of-line (EOL) resistors. EOL resistors are placed at the end of an activating device chain (i.e. pull station → pull station → smoke detector → pull station, or really any combination of activating devices) and allows for the detection of a line break within the system. This guarantees that the panel will detect if a device is no longer electrically connected to the panel, the panel can detect it and throw a trouble code. By extension, this means that the panel will always be able to read the device state, assuming no trouble codes are being ignored.

Due to voltage bleed in from poorly designed devices in a system, Antigneous has the ability to ignore some of that voltage to a certain extent. But enabling said feature reduces reliableness.

EEPROM
Antigneous makes use of the ESP-32 Dev Kit V1’s EEPROM to store user settings.
Antigneous EEPROM
Memory Address	Data Contained	Default Value	Possible Values
1-6	The string “Lexzach” to verify that this EEPROM was written by any version Antigneous FACP.	76, 101, 120, 122, 97, 99, 104	NA
7	Coding for NACs	0 (Code 3)	0 (Code 3) / 1 (Marchtime) / 2 (Code 4-4) / 3 (Continuous) / 4 (California Code) / 5 (Slow Marchtime)
8	Key switch requirement	0 (No key required)	0 (No key required) / 1 (Key required)
9	Verification	1 (Verification enabled)	0 (Verification disabled) / 1 (Verification enabled)
10	Verification time	25 (2.5 seconds)	1-255 (n*10 = Verification time in MS)
11-26	Panel name	65, 78, 84, 73, 71, 78, 69, 79, 85, 83, 32, 32, 32, 32, 32, 32 (ANTIGNEOUS followed by 6 blank characters)	0,32,45,46,47,48,49,50,51,52,53,54,55,56,57,65,66,67,68,69,70,71,72,73,74,75,76,77,78,79,80,81,82,83,84,85,86,87,88,89,90 for each address
50	EEPROM version	NA	0-255
51	EEPROM build	NA	0-255
72 DEPRECATED	EOL resistor lenience	125 (500)	0-255 (n*4 = usable resistor lenience)
73	EOL resistor enabled	1 (EOLR enabled)	0 (EOL resistor disabled) / 1 (EOL resistor enabled)
74	Pre-alarm	0 (Pre-alarm disabled)	0 (Pre-alarm disabled) / 1 (Pre-alarm enabled)
75	Pre-alarm first-stage time	1 (1 minute first-stage)	1-255 (Minutes for first-stage)
76	Smoke detector pre-alarm	0 (Smoke detector pre-alarm disabled)	0 (Smoke detector pre-alarm disabled) / 1 (Smoke detector pre-alarm enabled)
77	Smoke detector timeout	5 (Smoke detector timeout is 5 minutes)	0-255 (Smoke detector timeout in minutes)
78	Homescreen	0 (Panel name)	0 (not currently used)
79	Audible silence	1 (Audible silence enabled)	0 (Audible silence disabled) / 1 (Audible silence enabled)
80	LCD timeout	0 (LCD timeout disabled)	0-255 (n*15000 = LCD timeout in MS)

EEPROM Verification
On boot, Antigneous verifies the integrity of the EEPROM by checking the values of several memory addresses for invalid values. If any of the values are not as expected, Antigneous will display ERROR 1 and will prompt the user to check the manual. If the user presses the reset button, the panel will reset, if the user has not fixed the issue before pressing the reset button, the panel will most likely fail the validity check again. If the user presses the drill button, the panel will reset the EEPROM to factory defaults and perform a warm restart.
Antigneous EEPROM validity check routine
Memory Address	Expected Value
0	76
6	104
7	0, 1, 2, 3, 4, 5
8	0, 1
50	Current EEPROM version
51	Current EEPROM build

EEPROM Factory Reset Methods
In the case that the panel is inoperable, or the user wants to reset the panel to factory settings, Antigneous has multiple methods of resetting the EEPROM to a factory state.
Methods of resetting the Antigneous EEPROM
Holding down the silence, reset, and drill buttons during startup. This will prompt the user to continue holding down the buttons if they intend to perform a factory reset. The panel will wait 5 seconds after prompting the user, and if the user continues to hold down the buttons through the 5 seconds, the EEPROM will be reset. To prevent a state where the panel cannot be reset, either through a fault that prevents the panel from booting, or the key lock being toggled on without a key switch, resulting in a panel that would otherwise need to be re-flashed; Antigneous will not take the key switch into consideration when using this method to restore the EEPROM. The code for resetting the EEPROM via the buttons on startup is one of the first chunks of code executed on startup. Everything before it is code to setup pins and startup the serial monitor. This means that the three button EEPROM reset should be able to reset a panel no matter what state it is in.
Navigating to Settings > Panel > Factory Reset within the menu allows the user to reset the EEPROM from a running panel. Once the user confirms they wish to reset the EEPROM, the panel performs a factory reset routine and then warm reboots.
If the panel fails to verify the integrity of the EEPROM, the panel will display ERROR 1. Once displayed, the user can press the drill button to reset the panel to factory settings and then warm reboot.

Activating Device Check Routine
Antigneous polls activating devices with a 1 millisecond delay. Because poorly designed activating devices, namely (in testing) cheap smoke detectors may add residual voltage into the system at random intervals, which could be read from the panel as normal operation, when verification is enabled, Antigneous counts the amount of 0 readings it detects. Since a reading of 0 indicates beyond any doubt that there is a short in the activating circuit, and thus a device is activated, Antigneous counts the amount of zeros that occur within the specified verification time-frame, to determine whether or not to activate the NACs and enter full alarm. The ESP32 Dev Kit V1 reads voltage across a pin as a value between 0 and 4095. This does not correlate with voltage.
Antigneous Polling Voltages Under Ideal Circumstances
Reading Across Activating Device Loop	Meaning
0	Activated Device
4095	Ground fault / missing EOL
1-4094	Normal

To determine if the panel should enter full alarm, the panel does the following routine:
1. Count the amount of 0 readings during a specified time period set by the user, each check occurring every 1 millisecond.
2. During the last check in the time period, if the last check returns 0, continue to step 3, otherwise cancel.
3. Use the equation 0.1*verificationTime (in milliseconds) to determine how many 0 readings are required for activation.
Benefits of this routine:
- If an activating device adds residual power into the circuit at random intervals, this system of verification avoids a situation where, assuming the panel’s verification requires that the check returns only 0, the device adding random power into the system at a random point will constantly reset the panel verification due to some checks not returning 0.
Limitations of this routine:
- If the last check returns any value other than 0 because of a faulty device introducing power, the verification process will repeat until the last reading is 0. In testing, this has never occurred, but it is foreseeable that at some point, verification will take twice as long due to this issue.